## Heat Exchanger Function
Modeling a heat exchanger - The Logarithmic Mean Temperature Difference - WBLMTD
Keywords: Heat Exchanger, Log Mean Termperature Difference, LMTD;
A heat exchanger is a device for transfering heat from a hot fluid to a cold fluid. Examples are a car radiator, air conditioning coils, a gas powered
furnace, or various devices in an oil refinery and power plants. The amount of heat transfered in a small section of a heat exchanger is proportional
to (temperature difference between the two fluids)*(heat conductance of the separating material). If we can define a mean temperature
difference for the entire area or length of the heat exchanger, the total heat transferred is proportional to
Area*(heat conductance of the separating material)*(average temperature difference between the two fluids).
Case 3
Cool some fuel oil, from 185 to 140 F. We can do this by either using a lot of cooling water or an exchanger with large area.
Which combination should we use?
Counter Flow Heat Exchanger
| "THI" temperature of the hot fluid at its inlet (F) |  |  |  | "TCI" temperature of the cold fluid at its inlet (F)
| 185 |  |  |  | 50
| "THO" temperature of the hot fluid at its outlet (F) |  |  |  | "TCO" temperature of the cold fluid at its outlet (F)
| 140 |  |  |  | 1 | ? | <= | 95
| Temperature difference at the hot end |  |  |  | Temperature difference at the cold end |  |  |  | Note: a Parallel Flow would be:
| DTH = THI - TCO (F) |  |  |  | DTC = THO - TCI (F) |  |  |  |  | Temperature difference at the hot end, DTH = THI - TCI
| 184 |  |  |  | 90 |  |  |  |  | Temperature difference at the cold end, DTC = THO - TCO
|  |  | Counter flow heat exchanger schematic | [8 empty] | Parallel flow heat exchanger schematic
A simple estimate of the average temperature diffence is (DTH + DTC)/2. It has been found that for heat exhangers, a better estimate of the
average temperature difference is the Logarithmic Mean Temperature Difference = (DTH - DTC)/LOG( DTH/ DTC), or LMTD = WBLMTD(DTH, DTC)
Function WBLMTD (D1, D2)
131.4454
| "U" Heat transfer conductance (in BTU/(hr*sqfoot*degreesF)), sometimes called k value | [8 empty] | "A" Area (in square feet)
| 120 | [8 empty] | 1 | ? | <= | 155
| "HMASS" mass of hot fluid per unit time through exchanger ((in lb/hr) of hot fluid to be cooled) | [8 empty] | "HSPH" Specific heat of hot fluid (in BTU/(lb*DegreesFahrenheit))
| 50000 | [8 empty] | 0.74
| "CMASS" (in lb/hr) of cold fluid to be heated | [8 empty] | "CSPH" Specific heat of cold fluid (in BTU/(lb*degreesF))
| 1 | ? | <= | 43000 | [5 empty] | 1
| "ACOST" Relative cost of heat exchanger size | [8 empty] | "CCOST" Relative cost of cooling water
| 20 | [8 empty] | 1
A simple formulation as a model:
MIN = ACOST * A + CCOST * CMASS, Minimize combined cost
21
Calculations of quantity of heat transferred per unit time:
Quantity of heat transferred per unit time is the product of the conductivity * area * mean temperature difference: Q = U * A * MTD
15773.4422
Must = Quantity of heat lost per unit time by the hot fluid = mass of fluid per time * specific heat * temperature loss = Q = HMASS * HSPH * (THI - THO)
| 1665000 | Not =
Must = Quantity of heat gained per unit time by the cold fluid = Q = CMASS * CSPH * ( TCO - TCI)
| -49 | Not =
THI
TCO
TCO
TCI
TCI
THO
THI
TCI
TCI
TCO
TCO
THO

## Case 1 input
Case 1
100 liters per minute of water needs to be cooled from 90 C to 65 C, the cold fluid is water with an input temperature of 20 C.
The area of the heat exchanger is 4 m^2. The conductance is 1000 W/m^2*degrees C). Note that water is less dense at higher temperature.
How much cold water is needed? What will be its outlet temperature?
THI = 90 Hot fluid input temp (in degrees C)
THO = 65 Hot fluid output temp (in degrees C)
TCI = 20 Cold fluid input (in degrees C)
TCO = 50.1? Cold fluid is warmed up to (in degrees C)
U = 1000 Heat transfer conductance (in Joules/(sec*meter^2*degreesC))
A = 4 Area (in square meters)
HSPH = 4191 Specific heat of hot fluid (in Joules/(kg*DegreesC))
CSPH = 4175 Specific heat of cold fluid (in Joules/(kg*degreesC))
HMASS = 1.618333 (in kg/s) of hot fluid to be cooled = 100*0.971/60
CMASS = ? (in kg/s) of cold fluid to be heated

## Case 2 input
Case 2
Cool some fuel oil, What area is required and how much cooling water is needed?
THI = 185, Hot fluid input temp (in degrees F)
THO = 140 It must be cooled to (in degrees F)
TCI = 50 Cold fluid input (in degrees F)
TCO = 90 Cold fluid is warmed up to (in degrees F)
U = 120 Heat transfer conductance (in BTU/(hr*sqfoot*degreesF)), sometimes called k value
A = 150 Area (in square feet)
HSPH = 0.74 Specific heat of hot fluid (in BTU/(lb*DegreesFahrenheit))
CSPH = 1 Specific heat of cold fluid (in BTU/(lb*degreesF))
HMASS = 50000 (inlb/hr) of hot fluid to be cooled
CMASS = 41625 (in lb/hr) of cold fluid to be heated

## Case 3 input
Case 3
Cool some fuel oil, from 185 to 140 F. We can do this by either using a lot of cooling water or an exchanger with large area.
Which combination should we use?
THI = 185, Hot fluid input temp in degrees (F)
THO = 140, Hot fluid output temp,must be cooled to (in degrees F)
TCI = 50, Cold fluid input (in degrees F)
TCO = ?, Cold fluid output, is warmed up to (in degrees F)
U = 120, Heat transfer conductance (in BTU/(hr*sqfoot*degreesF)), sometimes called k value
A = ?, Area (in square feet)
HSPH = 0.74, Specific heat of hot fluid (in BTU/(lb*DegreesFahrenheit))
CSPH = 1, Specific heat of cold fluid (in BTU/(lb*degreesF))
HMASS = 50000, (in lb/hr) of hot fluid to be cooled
CMASS = ?, (in lb/hr) of cold fluid to be heated
CMASS <= 43000, Cannot use too much cooling water
A <= 155, Cannot use too big a heat exchanger
TCO <= 95, Cold water cannot be heated to high
ACOST = 20, Relative cost of heat exchanger size
CCOST = 1, Relative cost of cooling water
MIN = ACOST * A + CCOST * CMASS, Minimize combined cost